## Air Clean Time Required Calc
Air Changes and Time Required for Airborne Contaminant Removed by Efficiency
Input | Instructions
Output | To find CFM for a room enter room area and ceiling ht and required air changes.
Info | To find AC/HR for a room enterroom area and ceiling ht and CFM supplied to the room.
Use simple air change calculations to find air changes in space
and enter AC/HR in Find Time to clean chart to determine time based on room clean efficiency.
Simple Air Change CFM Calc
|  | Area | Height | AC/HR | CFM
| Find CFM | 100 | 9 | 6.94 | 104.1
| Find AC/H | 100 | 9 | 8.3333 | 125
Time to Clean
|  | Filter | AC/HR | Time
| Find Time | 99% | 7 | 40.5
|  | 99.9% | 7 | 60.5
99% Filter Time required for contaminant removal |  |  |  | 40.5 | Minutes
99.9% Filter Time required for contaminant removal |  |  |  | 60.5 | Minutes
Based on CDC Air Cleaning Chart

## Clean times
Updated 5-20-20
2 | 138
4 | 69
6 | 46
8 | 35
10 | 28
12 | 23
15 | 18
20 | 14
50 | 6
x | 7
x1 | 6
y1 | 46
x2 | 8
y2 | 35
y | 40.5
2 | 207
4 | 104
6 | 69
8 | 52
10 | 41
12 | 35
15 | 28
20 | 21
50 | 8
x | 7
x1 | 6
y1 | 69
x2 | 8
y2 | 52
y | 60.5